## Grid Booster
CPW Municipal Grid Booster TDH Calculator
Instructions: Fill in the black numbers in the domestic and fire columns and the results are automatically calculated and shown in the green rows.
Data Descriptions | Units of Measure | Domestic (Low Flow) | Fire (High Flow)
Elevation of the Highest Outlet | FEET | 1085.5 | 0
Elevation of Pump House Slab | FEET | 1003 | 0
Static Elevation Change | FEET | 82.5 | 0
Residual Pressure Required at the Highest Outlet | PSIG | 80 | 0
Design Flow Rate | GPM | 250 | 0
Discharge Piping Friction Loss | FEET | 80 | 0
Discharge Head Required | FEET | 347.3 | 0
Discharge Pressure Required | PSIG | 150.3809 | 0
Minimum Suction Pressure (at the design flow rate) | PSIG | 55 | 0
Maximum (Static) Suction Pressure | PSIG | 60
Carolina Pumpworks will fill in these numbers if unknown
Valve Losses at Pump System (Checks, PRV's, PCV,s, etc.) | PSIG | 3 | 3
Other losses at Pump System (Meters, Strainers, etc.) | PSIG | 0 | 0
Boost Pressure Required | PSIG | 98.3809 | 3
Pump TDH Required | FEET | 227.2599 | 6.93

## Plant Water
CPW Municipal Plant Water TDH Calculator
Instructions: Fill in the black numbers in the plant water column and the results are automatically calculated and shown in the green rows.
Data Descriptions | Units of Measure | Plant Water
Elevation of the Highest Outlet | FEET | 855
Elevation of Pump Room Floor | FEET | 834
Static Elevation Change | FEET | 21
Residual Pressure Required at the Highest Outlet | PSIG | 60
Design Flow Rate | GPM | 900
Discharge Piping Friction Loss | FEET | 16
Discharge Head Required | FEET | 175.6
Discharge Pressure Required | PSIG | 76.0348
Minimum Suction Pressure (at the design flow rate) | PSIG | 1
Maximum (Static) Suction Pressure | PSIG | 5
Carolina Pumpworks will fill in these numbers if unknown
Valve Losses at Pump System (Checks, PRV's, PCV,s, etc.) | PSIG | 3
Other losses at Pump System (Meters, Strainers, etc.) | PSIG | 0
Boost Pressure Required | PSIG | 78.0348
Pump TDH Required | FEET | 180.2604

## Tank Fill
CPW Municipal Tank Fill TDH Calculator
Instructions: Fill in the black numbers in the tank fill column and the results are automatically calculated and shown in the green rows.
Data Descriptions | Units of Measure | Tank Fill
Elevation of the "Pump Off" Tank Level | FEET | 928
Elevation of the "Pump On" Tank Level | FEET | 923
Elevation of the "Reserve" Tank Level | FEET | 918
Elevation of Pump House Slab | FEET | 834
Static Elevation Change | FEET | 94
Design Flow Rate | GPM | 700
Discharge Piping Friction Loss | FEET | 15
Discharge Head Required | FEET | 109
Discharge Pressure Required | PSIG | 47.197
Minimum Suction Pressure (at the design flow rate) | PSIG | 20
Maximum (Static) Suction Pressure | PSIG | 40
Carolina Pumpworks will fill in these numbers if unknown
Valve Losses at Pump System (Checks, PRV's, PCV,s, etc.) | PSIG | 3
Other losses at Pump System (Meters, Strainers, etc.) | PSIG | 0
Boost Pressure Required | PSIG | 30.197
Pump TDH Required | FEET | 69.7551